STATIONARY SYSTEM

FOR STATE BORDER

SURVEILLANCE

- Regional Border Police Centre towards the Republic of Romania

# SYSTEM DESIGN

July/August 2024

# Contents

1	PROJECT SCOPE	3

2	Regional Border Police Centre for surveillance of the state border with the Republic of Romania	3

2.1	Regional Centre (RCC) of the Border Police Directorate towards the Republic of Romania in Vršac	4

2.2	“Vrbica“ LOCATION	6

2.3	"Kikinda 2” LOCATION - radio relay point	9

2.4	“Srpska Crnja“ LOCATION	10

2.5	“Kikinda Police Administration” LOCATION - radio relay point	13

2.6	“Jaša Tomić“ LOCATION	14

2.7	“Krajišnik” LOCATION - radio relay point	16

2.8	“Veliki Gaj“ LOCATION	17

2.9	“Vršački Breg” LOCATION - radio relay point	21

2.10	“Bela Crkva” LOCATION - radio relay point	22

2.11	“Kusić“ LOCATION	23

2.12	“BPS in Veliko Gradište“ LOCATION	26

3	COMPREHENSIVE LIST OF REQUIRED EQUIPMENT	28

# PROJECT SCOPE

As part of this Project, it is necessary to install 5 stationary systems for state border surveillance on the border between the Republic of Serbia and the Republic of Romania.

Within this Project, the area of ​​the state border between the Republic of Serbia and the Republic of Romania falls within the competence of the Regional Border Police Centre towards the Republic of Romania with its central office in Vršac, 14 Anđe Ranković Street, where the Regional Coordination Centre (RCC) will be established for all locations in this part of the state border (locations: "Vrbica", "Srpska Crnja", "Jaša Tomić", " Plandište" and "Kusić"). In addition to the Regional Centre, a local surveillance centre (LSC) will be established in this part of the state border in the Veliko Gradište Border Police Station, 9 Obala Kralja Petra I Street.

For the purpose of this project, the supplier will be obliged to equip the aforementioned two centres, each with one set for monitoring the operation of stationary systems for state border surveillance with thermal imaging, day/night cameras (Multisensor), each set comprising one /1/ computer with three /3/ desktop monitors of minimum 23.5", joystick for managing video surveillance systems, accompanying application software for monitoring the operation of stationary systems at the state border. One /1/ wall-mounted video screen of minimum 65" will be installed in each centre.

# Regional Border Police Centre for surveillance of the state border with the Republic of Romania

The Regional Border Police Centre towards the Republic of Romania is organised for the area on the part of the state border between the Republic of Serbia and the Republic of Romania, with the central office in Vršac.

Within this Project, five locations for stationary systems have been defined in the given area:

- “Vrbica“ (46° 1'17.97"N 20°18'50.94"E)

- “Srpska Crnja“ (45°44'56.81"N 20°41'58.71"E)

- “Jaša Tomić“ (45°28'14.52"N 20°50'56.18"E)

- “Veliki Gaj“ (45°17'48.13"N 21°10'0.30"E)

- “Kusić“ (44°52'25.00"N 21°29'54.81"E)

In addition to these locations, as part of this Project, the following locations will be equipped with communication equipment that will be used to connect the stationary systems for state border surveillance to the telecommunications system of the Ministry of Interior of the Republic of Serbia and enable signal distribution:

- Bela Crkva (44°54'07.5"N 21°24'18.7"E)

- Vršački Breg (45°07'22.1"N 21°19'29.9"E)

- Krajišnik (45°26'55.70"N, 20°43'2.80"E)

- Kikinda 2 (45°50'19.28"N, 20°29'02.02"E)

- Police Administration in Kikinda, 5 Braće Tatić Street

## Regional Centre (RCC) of the Border Police Directorate towards the Republic of Romania in Vršac

The Regional Coordination Centre (RCC) for the protection of the state border with the Republic of Romania is planned to be built in the regional centre. For this purpose, it is necessary to provide one set for monitoring the operation of stationary systems for state border surveillance.

Furthermore, it is necessary to provide a UPS device for uninterrupted power supply in order for the Centre to be functional even in the event of a power outage. In the area (RCC) where the workstation and LCD TV are being installed, it is necessary to perform the installation of high and low current.

The installation of low current should be carried out in such a manner as to provide six RJ45 connectors. The connectors are installed in such a manner that the UTP cable Cat. 6 runs from the room of the RCC to the communication cabinet in the border police facility. UTP cables are laid in wall ducts and end on one side at wall sockets, and on the other at the patch panel with the corresponding number of ports in the communication cabinet. The installed connectors must be marked, and measurements must be made to determine the quality of the installations. The average distance between the RCC room and the communication cabinet is 60 meters.

The installation of high current should be carried out in such a manner to provide four 230V connectors. The connectors are installed so that the power cables are run through from the RCC room to the nearest power distribution cabinet in the regional centre building. Power cables are run through the wall ducts and end in wall sockets on one side, and on a separate fuse in the distribution cabinet. The connector in the distribution cabinet is installed from the field for aggregate power supply (if there is one). The power of installed connectors must be sufficient to power a UPS device of at least 4.5 kW. Installed connectors must be marked. The average distance between the RCC room and the current distribution cabinet is 50 meters.

The supplier will be obliged to set up one radio-relay link of 100 Mbit/s at the location of the Regional Centre in Vršac which will connect the Regional Surveillance Centre (RCC) with the "Vršački Breg” location. Furthermore, the radio-relay device from the Regional Centre in Vršac will be connected to the network of the Ministry of Interior, which will enable the distribution of video signals to the central server.

The radio link for connecting the RCC with stationary video surveillance system

In order to finalise the communication connection of the Regional Centre of the Border Police in Vršac with the location of "Vršački Breg", it is necessary to place a 5m high metal pole on the roof of the Regional Centre on which the radio-relay link will be mounted.

Conclusion:

At the location of the Regional Border Police Centre in Vršac towards the Republic of Romania, the following utems must be delivered and installed:

1. One workstation with accompanying surveillance software

2. Three monitors of minimum 23.5"

3. One LCD screen on the wall, of minimum 65"

4. One UPS

5. One desk

6. Two chairs

7. High and low current installation

8. One cabinet

9. One side of a 100 Mbit/s radio link to connect this location with the Vršački Breg location

10. One metal pole of 5m

## “Vrbica“ LOCATION

"Vrbica" (46° 1'17.97"N 20°18'50.94"E) is located in the village of Vrbica, Municipality of Čoka.

The management of the cameras at the "Vrbica" location would be carried out from the Regional Surveillance Centre (RCC) in the Regional Border Police Centre towards the Republic of Romania in Vršac and the Local Border Police Centre in Veliko Gradište.

It is necessary to envisage the procurement, delivery and installation of a steel telecommunications pole with a 24-meter-high platform and an adequate communication cabinet for external installation, dimensioned in such manner that it is possible to place all the necessary equipment on site.

During the construction of the pole, it is necessary to comply with all valid legal documents and by-laws pertaining to the design and construction of steel structures.

Before the construction of the pole, it is necessary to build the foundation for the pole and the grounding of the lightning rod on the site, which includes all construction and craft work (earthwork, concrete work, reinforcement, locksmithing, etc.), work on the electrical installation of high and low current, and work on the installation of grounding and lightning protection. All the abovementioned works must be carried out before the delivery and installation of the border surveillance equipment.

Before mounting the equipment on the pole, it is necessary to bring the electrical installation to each device that is envisaged for this location within the project, as well as to bring the telecommunications installation from the communication cabinet that will be located on the pole to each device that is envisaged for this location within the project.

The telecommunications pole must be painted red and white.

On the pole built in this manner, the supplier will be obliged to install a medium-range stationary system (thermal imaging camera - day/night camera) and a radio-relay link antenna at the height required to establish a high-quality radio connection with the "Kikinda 2" location (45°50'19.28"N, 20°29'02.02"E).

At the location, the supplier will be obliged to install a 15U watertight communication cabinet for external mounting on the structure of the pole at a height of 1.5 meters from the foundation and place all the necessary equipment referred to in this project in it. The cabinet must be supplied with a humidity/temperature regulator (Hygrostat) that controls the heating and cooling of the cabinet in cases where the relative humidity exceeds the value set on the device. This prevents the relative humidity of the air from staying above the dew and condensation point. The built-in components and the cabinet itself are protected in this way. Such device combines the function of a thermostat and a hygrostat in one case, and at the same time independently monitors the relative humidity and temperature inside the cabinet. The cabinet must be delivered with an air conditioning unit and must also have a programmable thermostat. The air conditioning unit must be designed for external installation with a minimum cooling power of >850W. The air conditioning unit is mounted on the side of the cabinet, which must be prepared for the air conditioning unit at the factory. IP protection of the air conditioning unit, minimum IP55. Ambient operating temperature for air conditioning unit of minimum -15 °C to +50 °C. The air conditioning unit must be equipped with fans with a minimum air flow of 500m3/h.

It is necessary to install a switch, UPS and WEB relay in the cabinet on the pole, with at least 4 controllable switches, which would enable remote switching on and off of the equipment.

A solid wire panel fence with a minimum height of 2 meters and a wire of at least 5 mm thick must be erected around the entire building. The distance between the fence and the post must be of at least 2 m.  The space inside the fence must be filled with material that prevents the growth of plants. There must be a gate with a lock on the fence, at least 1m wide. Panels and posts must be protected by hot-dip galvanising and then plasticised for additional protection from

corrosion. The entire perimeter of the fence must be monitored with a minimum of four WDR Bullet IP cameras with a minimum resolution of 2 Mpix.

From this location, the footage from the medium-range stationary system will be monitored in RBPC in Vršac, BPS (border police station) in Veliko Gradište and the head office of the MoI, so the supplier will be obliged to install one side of the 100 Mbit/s radio relay link at this location, which will connect the location of "Vrbica" with the location of "Kikinda 2" (45°50'19.28"N, 20°29'02.02"E).

Vrbica-Kikinda 2 Radio relay link

Video streams from this location would be recorded in the best quality at the central location of the Ministry of Interior of the Republic of Serbia in Belgrade on the central server for video surveillance, and streams of lower quality (minimum 720p) would be transmitted in real time from the central video server, through the telecommunications system of the Ministry of Interior, to the RBPC in Vršac and BPS in Velko Gradište.

For the purpose of calculating the capacity of the IT network, in order to transmit the video signal of cameras in real time at a minimum of 720p, a maximum of 3 Mb/s transmission path per video channel shall be available. A stationary system that needs more than 3 Mb/s transmission path, for the transmission of a video signal of 720p quality in real time, shall not be acceptable to the ordering party.

Conclusion:

At this location of "Vrbica", it is necessary to deliver and install the following items:

1.	One medium-range stationary system (thermal imaging camera + day/night camera)

2. four WDR Bullet IP cameras

3. one switch

4. one WEB relay

5.	One UPS 19" rack

6.	One side of the radio relay link with a capacity of 100 Mbit/s to connect this location with the "Kikinda 2" location

7.	One 15U communication cabinet for external mounting with air conditioning

8.	One steel telecommunications pole of 24m with foundations (lattice with platform)

9.	Wire panel fence with gate and backfilling of the fenced area

## "Kikinda 2” LOCATION - radio relay point

At the location of "Kikinda 2" (45°50'19.28"N, 20°29'02.02"E) there is a silo with a room where the telecommunications equipment of the Ministry of Interior of the Republic of Serbia is located, and the Ministry of Interior has a contract with the owner regarding the use of the location in the field of telecommunications. For this Project, this location would become a radio-relay connection point for the stationary systems from the "Vrbica" and "Srpska Crnja" locations with the Kikinda Police Administration location.

For this purpose, it is necessary to establish the following radio relay links:

- Location of "Vrbica" - location of "Kikinda 2"

- Location of "Srpska Crnja" - location of "Kikinda 2"

- Location of  “Kikinda Police Administration" - location of "Kikinda 2"

In this regard, it is necessary to place a 5m high metal pole at the "Kikinda 2" location on which the radio-relay links, with a capacity of 100 Mb/s, will be installed. The internal equipment units are mounted in the existing communication cabinet of the Ministry of Interior of Serbia.

Kikinda 2

Conclusion:

At the location of "Kikinda 2", it is necessary to deliver and install the following items:

- One side of the radio relay link of 100 Mb/s, connection to the "Vrbica” location

- One side of the radio relay link of 100 Mb/s, connection to the "Srpska Crnja” location

- One side of the radio relay link of 100 Mb/s, connection to the "Kikinda Police Administration” location

- One 5m metal pole on the roof of the silo

## “Srpska Crnja“ LOCATION

The location of "Srpska Crnja" (45°44'56.81"N 20°41'58.71"E) belongs to the Srpska Crnja settlement, Municipality of Nova Crnja.

The management of the cameras at the "Srpska Crnja" location would be carried out from the Regional Surveillance Centre (RCC) in the Regional Border Police Centre towards the Republic of Romania in Vršac and the Local Border Police Centre in Veliko Gradište.

It is necessary to envisage the procurement, delivery and installation of a steel telecommunications pole with a 24-meter-high platform and an adequate communication cabinet for external installation, dimensioned in such manner that it is possible to place all the necessary equipment on site.

During the construction of the pole, it is necessary to comply with all valid legal documents and by-laws pertaining to the design and construction of steel structures.

Before the construction of the pole, it is necessary to build the foundation for the pole and the grounding of the lightning rod on the site, which includes all construction and craft work (earthwork, concrete work, reinforcement, locksmithing, etc.), work on the electrical installation of high and low current, and work on the installation of grounding and lightning protection. All the abovementioned works must be carried out before the delivery and installation of the border surveillance equipment.

Before mounting the equipment on the pole, it is necessary to bring the electrical installation to each device that is envisaged for this location within the project, as well as to bring the telecommunications installation from the communication cabinet that will be located on the pole to each device that is envisaged for this location within the project.

The telecommunications pole must be painted red and white.

On the pole built in this manner, the supplier will be obliged to install a medium-range stationary system (thermal imaging camera - day/night camera) and a radio-relay link antenna at the height required to establish a high-quality radio connection with the "Kikinda 2" location (45°50'19.28"N, 20°29'02.02"E).

At the location, the supplier will be obliged to install a 15U watertight communication cabinet for external mounting on the structure of the pole at a height of 1.5 meters from the foundation and place all the necessary equipment referred to in this project in it. The cabinet must be supplied with a humidity/temperature regulator (Hygrostat) that controls the heating and cooling of the cabinet in cases where the relative humidity exceeds the value set on the device. This prevents the relative humidity of the air from staying above the dew and condensation point. The built-in components and the cabinet itself are protected in this way. Such device combines the function of a thermostat and a hygrostat in one case, and at the same time independently monitors the relative humidity and temperature inside the cabinet. The cabinet must be delivered with an air conditioning unit and

must also have a programmable thermostat. The air conditioning unit must be designed for external installation with a minimum cooling power of >850W. The air conditioning unit is mounted on the side of the cabinet, which must be prepared for the air conditioning unit at the factory. IP protection of the air conditioning unit, minimum IP55. Ambient operating temperature for air conditioning unit of minimum -15 °C to +50 °C. The air conditioning unit must be equipped with fans with a minimum air flow of 500m3/h.

It is necessary to install a switch, UPS and WEB relay in the cabinet on the pole, with at least 4 controllable switches, which would enable remote switching on and off of the equipment.

A solid wire panel fence with a minimum height of 2 meters and a wire of at least 5 mm thick must be erected around the entire building. The distance between the fence and the post must be of at least 2 m. The space inside the fence must be filled with material that prevents the growth of plants. There must be a gate with a lock on the fence, at least 1m wide. Panels and posts must be protected by hot-dip galvanising and then plasticised for additional protection from corrosion. The entire perimeter of the fence must be monitored with a minimum of four WDR Bullet IP cameras with a minimum resolution of 2 Mpix.

From this location, the footage from the medium-range stationary system will be monitored in RBPC in Vršac, BPS (border police station) in Veliko Gradište and the head office of the MoI, so the supplier will be obliged to install one side of the 100 Mbit/s radio relay link at this location, which will connect the location of "Srpska Crnja" with the location of "Kikinda 2" (45°50'19.28"N, 20°29'02.02"E).

Srpska Crnja - Kikinda 2 radio relay link

Video streams from this location would be recorded in the best quality at the central location of the Ministry of Internal Affairs of the Republic of Serbia in Belgrade on the central server for video

surveillance, and streams of lower quality (minimum 720p) would be transmitted in real time from the central video server, through the telecommunications system of the Ministry of Interior, to RBPC in Vršac and BPS in Velko Gradište.

For the purpose of calculating the capacity of the IT network, in order to transmit the video signal of cameras in real time at a minimum of 720p, a maximum of 3 Mb/s transmission path per video channel shall be available. A stationary system that needs more than 3 Mb/s transmission path, for the transmission of a video signal of 720p quality in real time, shall not be acceptable to the ordering party.

Conclusion:

At this location of "Vrbica", it is necessary to deliver and install the following items:

1.	One medium-range stationary system (thermal imaging camera + day/night camera)

2. four WDR Bullet IP cameras

3. one switch

4. one WEB relay

5.	One UPS 19" rack

6.	One side of the radio relay link with a capacity of 100 Mbit/s to connect this location with the "Kikinda 2" location

7.	One 15U communication cabinet for external mounting with air conditioning

8.	One steel telecommunications pole of 24m with foundations (lattice with platform)

9.	Wire panel fence with gate and backfilling of the fenced area

## “Kikinda Police Administration” LOCATION - radio relay point

For this project, the “Kikinda Police Administration“ location (5 Braće Tatić Street) would be a radio-relay connection point for the stationary systems from the "Vrbica" and "Srpska Crnja" locations, via the "Kikinda 2" location, to the Ministry's telecommunications network.

For this purpose, it is necessary to establish the following radio relay link:

- Location of  “Kikinda Police Administration" - location of "Kikinda 2"

In this regard, it is necessary to place a 5m high metal pole at the "Kikinda Police Administration" location on which the radio-relay link with a capacity of 100 Mb/s, will be installed. The internal unit of the equipment is mounted in the existing communication cabinet of the MoI of Serbia.

Kikinda Police Administration -Kikinda 2 radio-relay link

Conclusion:

At the location of "Kikinda Police Administration", it is necessary to deliver and install the following items:

- One side of the radio relay link of 100 Mb/s, connection to the "Kikinda2” location

- One 5m metal pole on the roof of the building

## “Jaša Tomić“ LOCATION

“Jaša Tomić“ location (45°28'14.52"N 20°50'56.18"E) belongs to the Municipality of Sečanj. For this Project, this location would also become a radio-relay connection point for the stationary system from the "Veliki Gaj" location (45°17'48.13"N 21°10'0.30"E).

The management of the cameras at the "Jaša Tomić" location would be carried out from the Regional Surveillance Centre (RCC) in the Regional Border Police Centre towards the Republic of Romania in Vršac and the Local Border Police Centre in Veliko Gradište.

It is necessary to envisage the procurement, delivery and installation of a steel telecommunications pole with a 24-meter-high platform and an adequate communication cabinet for external installation, dimensioned in such manner that it is possible to place all the necessary equipment on site.

During the construction of the pole, it is necessary to comply with all valid legal documents and by-laws pertaining to the design and construction of steel structures.

Before the construction of the pole, it is necessary to build the foundation for the pole and the grounding of the lightning rod on the site, which includes all construction and craft work (earthwork, concrete work, reinforcement, locksmithing, etc.), work on the electrical installation of high and low current, and work on the installation of grounding and lightning protection. All the abovementioned works must be carried out before the delivery and installation of the border surveillance equipment.

Before mounting the equipment on the pole, it is necessary to bring the electrical installation to each device that is envisaged for this location within the project, as well as to bring the telecommunications installation from the communication cabinet that will be located on the pole to each device that is envisaged for this location within the project.

The telecommunications pole must be painted red and white.

On the pole built in this manner, the supplier will be obliged to install a medium-range stationary system (thermal imaging camera - day/night camera) and a radio-relay link antenna at the height required to establish a high-quality radio connection with the “Krajišnik“ location (45°26'55.70"N, 20°43'2.80"E).

At the location, the supplier will be obliged to install a 15U watertight communication cabinet for external mounting on the structure of the pole at a height of 1.5 meters from the foundation and place all the necessary equipment referred to in this project in it. The cabinet must be supplied with a humidity/temperature regulator (Hygrostat) that controls the heating and cooling of the cabinet in cases where the relative humidity exceeds the value set on the device. This prevents the relative humidity of the air from staying above the dew and condensation point. The built-in components and the cabinet itself are protected in this way. Such device combines the function of a thermostat and a hygrostat in one case, and at the same time independently monitors the relative humidity and temperature inside the cabinet. The cabinet must be delivered with an air conditioning unit and must also have a programmable thermostat. The air conditioning unit must be designed for external installation with a minimum cooling power of >850W. The air conditioning unit is mounted on the side of the cabinet, which must be prepared for the air conditioning unit at the factory. IP protection of the air conditioning unit, minimum IP55. Ambient operating temperature for air conditioning unit of minimum -15 °C to +50 °C. The air conditioning unit must be equipped with fans with a minimum air flow of 500m3/h.

It is necessary to install a switch, UPS and WEB relay in the cabinet on the pole, with at least 4 controllable switches, which would enable remote switching on and off of the equipment.

A solid wire panel fence with a minimum height of 2 meters and a wire of at least 5 mm thick must be erected around the entire building. The distance between the fence and the post must be of at least 2 m.  The space inside the fence must be filled with material that prevents the growth of plants. There must be a gate with a lock on the fence, at least 1m wide. Panels and posts must be protected by hot-dip galvanising and then plasticised for additional protection from corrosion. The entire perimeter of the fence must be monitored with a minimum of four WDR Bullet IP cameras with a minimum resolution of 2 Mpix.

From this location, the footage from the medium-range stationary system will be monitored in RBPC in Vršac, BPS (border police station) in Veliko Gradište and the head office of the MoI, so the supplier will be obliged to install one side of the 100 Mbit/s radio relay link at this location, which will connect the location of "Jaša Tomić" with the location of "Krajišnik“ (45°26'55.70"N, 20°43'2.80"E), where the entry point into the MoI network will be located. In addition, at this location, the supplier will be obliged to install one side of the 100 Mbit/s radio relay link, which will connect the location of "Jaša Tomić" with the location of "Veliki Gaj" (45°17'48.13"N 21°10'0.30"E)

Jaša Tomić – Krajišnik radio relay link

Jaša Tomić – Veliki Gaj radio relay link

Video streams from this location would be recorded in the best quality at the central location of the Ministry of Interior of the Republic of Serbia in Belgrade on the central server for video surveillance, and streams of lower quality (minimum 720p) would be transmitted in real time from the central video server, through the telecommunications system of the Ministry of Interior, to the RBPC in Vršac and BPS in Velko Gradište.

For the purpose of calculating the capacity of the IT network, in order to transmit the video signal of cameras in real time at a minimum of 720p, a maximum of 3 Mb/s transmission path per video channel shall be available. A stationary system that needs more than 3 Mb/s transmission path, for the transmission of a video signal of 720p quality in real time, shall not be acceptable to the ordering party.

Conclusion:

At this location of "Jaša Tomić", it is necessary to deliver and install the following items:

1.	One medium-range stationary system (thermal imaging camera + day/night camera)

2. four WDR Bullet IP cameras

3. one switch

4. one WEB relay

5.	One UPS 19" rack

6.	One side of the radio relay link with a capacity of 100 Mbit/s to connect this location with the "Krajišnik" location

7. 	One side of the radio relay link with a capacity of 100 Mbit/s to connect this location with the "Veliki Gaj" location

8.	One 15U communication cabinet for external mounting with air conditioning

9.	One steel telecommunications pole of 24m with foundations (lattice with platform)

10.	Wire panel fence with gate and backfilling of the fenced area

## “Krajišnik” LOCATION - radio relay point

At the location of "Krajišnik“ (45°26'55.70"N, 20°43'2.80"E) there is a silo with an external cabinet where the telecommunications equipment of the Ministry of Interior of the Republic of Serbia is located, and the Ministry of Interior has a contract with the owner regarding the use of the location in the field of telecommunications. For this Project, this location would become a radio relay point connecting stationary video surveillance systems to the Ministry's telecommunications network.

Krajišnik silo

For this purpose, it is necessary to establish the following radio relay link:

- "Jaša Tomić” location  - "Krajišnik” location

In this regard, it is necessary to place a 5m high metal pole at the "Krajišnik" location on which the radio-relay link with a capacity of 100 Mb/s, will be installed. The internal unit of the equipment is mounted in the existing communication cabinet of the MoI of Serbia.

Jaša Tomić – Krajišnik radio relay link

Conclusion:

At the location of "Krajišnik", it is necessary to deliver and install the following items:

- One side of the radio relay link of 100 Mb/s, connection to the "Jaša Tomić” location

- One 5m metal pole on the roof of the building

## “Veliki Gaj“ LOCATION

The location of "Veliki Gaj" (45°17'48.13"N 21°10'0.30"E) belongs to the agricultural district of the village of Veliki Gaj, Municipality of Plandište. For this Project, this location would also become a radio-relay connection point for the stationary system from the "Jaša Tomić“ location (45°17'48.13"N 21°10'0.30"E).

The management of the cameras at the "Veliki Gaj" location would be carried out from the Regional Surveillance Centre (RCC) in the Regional Border Police Centre towards the Republic of Romania in Vršac and the Local Border Police Centre in Veliko Gradište.

It is necessary to envisage the procurement, delivery and installation of a steel telecommunications pole with a 24-meter-high platform and an adequate communication cabinet for external installation, dimensioned in such manner that it is possible to place all the necessary equipment on site.

During the construction of the pole, it is necessary to comply with all valid legal documents and by-laws pertaining to the design and construction of steel structures.

Before the construction of the pole, it is necessary to build the foundation for the pole and the grounding of the lightning rod on the site, which includes all construction and craft work (earthwork, concrete work, reinforcement, locksmithing, etc.), work on the electrical installation of high and low current, and work on the installation of grounding and lightning protection. All the abovementioned works must be carried out before the delivery and installation of the border surveillance equipment.

Before mounting the equipment on the pole, it is necessary to bring the electrical installation to each device that is envisaged for this location within the project, as well as to bring the telecommunications installation from the communication cabinet that will be located on the pole to each device that is envisaged for this location within the project.

The telecommunications pole must be painted red and white.

On the pole built in this manner, the supplier will be obliged to install a medium-range stationary system (thermal imaging camera - day/night camera) and a radio-relay link antenna at the height required to establish a high-quality radio connection with the “Vršački Breg“ location (45°07'22.1"N 21°19'29.9"E).

At the location, the supplier will be obliged to install a 15U watertight communication cabinet for external mounting on the structure of the pole at a height of 1.5 meters from the foundation and place all the necessary equipment referred to in this project in it. The cabinet must be supplied with a humidity/temperature regulator (Hygrostat) that controls the heating and cooling of the cabinet in cases where the relative humidity exceeds the value set on the device. This prevents the relative humidity of the air from staying above the dew and condensation point. The built-in components and the cabinet itself are protected in this way. Such device combines the function of a thermostat and a hygrostat in one case, and at the same time independently monitors the relative humidity and temperature inside the cabinet. The cabinet must be delivered with an air conditioning unit and must also have a programmable thermostat. The air conditioning unit must be designed for external installation with a minimum cooling power of >850W. The air conditioning unit is mounted on the side of the cabinet, which must be prepared for the air conditioning unit at the factory. IP protection of the air conditioning unit, minimum IP55. Ambient operating temperature for air conditioning unit of minimum -15 °C to +50 °C. The air conditioning unit must be equipped with fans with a minimum air flow of 500m3/h.

It is necessary to install a switch, UPS and WEB relay in the cabinet on the pole, with at least 4 controllable switches, which would enable remote switching on and off of the equipment.

A solid wire panel fence with a minimum height of 2 meters and a wire of at least 5 mm thick must be erected around the entire building. The distance between the fence and the post must be of at least 2 m. The space inside the fence must be filled with material that prevents the growth of plants. There must be a gate with a lock on the fence, at least 1m wide. Panels and posts must be protected by hot-dip galvanising and then plasticised for additional protection from corrosion. The entire perimeter of the fence must be monitored with a minimum of four WDR Bullet IP cameras with a minimum resolution of 2 Mpix.

From this location, the footage from the medium-range stationary system will be monitored in RBPC in Vršac, BPS (border police station) in Veliko Gradište and the head office of the MoI, so the supplier will be obliged to install one side of the 100 Mbit/s radio relay link at this location, which will connect the location of "Veliki Gaj" with the location of "Vršački Breg". In addition, at this location, the supplier will be obliged to install one side of the 100 Mbit/s radio relay link, which will connect the location of "Jaša Tomić" with the location of "Veliki Gaj".

Veliki Gaj – Vršački Breg radio relay link

Veliki Gaj – Jaša Tomić radio relay link

Video streams from this location would be recorded in the best quality at the central location of the Ministry of Interior of the Republic of Serbia in Belgrade on the central server for video surveillance, and streams of lower quality (minimum 720p) would be transmitted in real time from the central video server, through the telecommunications system of the Ministry of Interior, to the RBPC in Vršac and BPS in Velko Gradište.

For the purpose of calculating the capacity of the IT network, in order to transmit the video signal of cameras in real time at a minimum of 720p, a maximum of 3 Mb/s transmission path per video channel shall be available. A stationary system that needs more than 3 Mb/s transmission path, for the transmission of a video signal of 720p quality in real time, shall not be acceptable to the ordering party.

Conclusion:

At this location of "Veliki Gaj", it is necessary to deliver and install the following items:

1.	One medium-range stationary system (thermal imaging camera + day/night camera)

2. four WDR Bullet IP cameras

3. one switch

4. one WEB relay

5.	One UPS 19" rack

6.	One side of the radio relay link with a capacity of 100 Mbit/s to connect this location with the "Jaša Tomić" location

7. 	One side of the radio relay link with a capacity of 100 Mbit/s to connect this location with the "Vršački Breg" location

8.	One 15U communication cabinet for external mounting with air conditioning

9.	One steel telecommunications pole of 24m with foundations (lattice with platform)

10.	Wire panel fence with gate and backfilling of the fenced area

## “Vršački Breg” LOCATION - radio relay point

For the purpose of this Project, the location of "Vršački Breg" (45°07'22.1"N 21°19'29.9"E) would be the radio-relay point of connection of stationary systems from the locations of "Veliki Gaj", "RBPC in Vršac", as well as the radio-relay point "Bela Crkva" to the telecommunications network of the Ministry. The given location belongs to the PE “Emisiona Tehnika i Veze”, with which the Ministry of Interior has concluded a contract in the field of telecommunications and installation of equipment at emission locations.

For this purpose, it is necessary to establish the following radio relay links:

- “Veliki Gaj“ location – “Vršački Breg“ location

- “RBPC in Vršac“ location – “Vršački Breg“ location

- “Bela Crkva“ location – “Vršački Breg“ location

The internal unit of the equipment is mounted in the existing communication cabinet of the MoI of Serbia in the constructed facility.

Vršački Breg

Conclusion:

At the location of "Vršački Breg", it is necessary to deliver and install the following items:

- One side of the radio relay link of 100 Mb/s, connection to the "Veliki Gaj” location

- One side of the radio relay link of 100 Mb/s, connection to the "RBPC in Vršac” location

- One side of the radio relay link of 100 Mb/s, connection to the "Bela Crkva” location

## “Bela Crkva” LOCATION - radio relay point

For the purpose of this Project, the location of "Bela Crkva" (44°54'07.5"N 21°24'18.7"E) would be the radio-relay connection point of the stationary system from the location of "Kusić". The Ministry of Interior has concluded a contract with the owner of the building regarding the use of the location in the field of telecommunications and the installation of equipment.

For this purpose, it is necessary to establish the following radio relay links:

- “Bela Crkva“ location – “Vršački Breg“ location

- “Bela Crkva“ location – “Kusić“ location

Vršački Breg-Bela Crkva radio relay link

The internal unit of the equipment is mounted in the existing communication cabinet of the MoI of Serbia on the silo.

Bela Crkva

Conclusion:

At the location of "Bela Crkva", it is necessary to deliver and install the following items:

- One side of the radio relay link of 100 Mb/s, connection to the "Kusić” location

- One side of the radio relay link of 100 Mb/s, connection to the "Vršački Breg” location

- One 5m metal pole on the roof of the building

## “Kusić“ LOCATION

Location of "Kusić" (44°52'25.00"N 21°29'54.81"E) belongs to the Kusić settlement, Municipality of Bela Crkva.

The management of the cameras at the "Kusić" location would be carried out from the Regional Surveillance Centre (RCC) in the Regional Border Police Centre towards the Republic of Romania in Vršac and the Local Border Police Centre in Veliko Gradište.

It is necessary to envisage the procurement, delivery and installation of a steel telecommunications pole with a 24-meter-high platform and an adequate communication cabinet for external installation, dimensioned in such manner that it is possible to place all the necessary equipment on site.

During the construction of the pole, it is necessary to comply with all valid legal documents and by-laws pertaining to the design and construction of steel structures.

Before the construction of the pole, it is necessary to build the foundation for the pole and the grounding of the lightning rod on the site, which includes all construction and craft work (earthwork, concrete work, reinforcement, locksmithing, etc.), work on the electrical installation of high and low current, and work on the installation of grounding and lightning protection. All the abovementioned works must be carried out before the delivery and installation of the border surveillance equipment.

Before mounting the equipment on the pole, it is necessary to bring the electrical installation to each device that is envisaged for this location within the project, as well as to bring the telecommunications installation from the communication cabinet that will be located on the pole to each device that is envisaged for this location within the project.

The telecommunications pole must be painted red and white.

On top of the pole built in this manner, the supplier will be obliged to install a medium-range stationary system (thermal imaging camera - day/night camera) and a radio-relay link antenna at the height required to establish a high-quality radio connection with the "Vršački Breg" location.

At the location, the supplier will be obliged to install a 15U watertight communication cabinet for external mounting on the structure of the pole at a height of 1.5 meters from the foundation and place all the necessary equipment referred to in this project in it. The cabinet must be supplied with a humidity/temperature regulator (Hygrostat) that controls the heating and cooling of the cabinet in cases where the relative humidity exceeds the value set on the device. This prevents the relative humidity of the air from staying above the dew and condensation point. The built-in components and the cabinet itself are protected in this way. Such device combines the function of a thermostat and a hygrostat in one case, and at the same time independently monitors the relative humidity and temperature inside the cabinet. The cabinet must be delivered with an air conditioning unit and must also have a programmable thermostat. The air conditioning unit must be designed for external installation with a minimum cooling power of >850W. The air conditioning unit is mounted on the side of the cabinet, which must be prepared for the air conditioning unit at the factory. IP protection of the air conditioning unit, minimum IP55. Ambient operating temperature for air conditioning unit of minimum -15 °C to +50 °C. The air conditioning unit must be equipped with fans with a minimum air flow of 500m3/h.

It is necessary to install a switch, UPS and WEB relay in the cabinet on the pole, with at least 4 controllable switches, which would enable remote switching on and off of the equipment.

A solid wire panel fence with a minimum height of 2 meters and a wire of at least 5 mm thick must be erected around the entire building. The distance between the fence and the post must be of at least 2 m.  The space inside the fence must be filled with material that prevents the growth of plants. There must be a gate with a lock on the fence, at least 1m wide. Panels and posts must be protected by hot-dip galvanising and then plasticised for additional protection from corrosion. The entire perimeter of the fence must be monitored with a minimum of four WDR Bullet IP cameras with a minimum resolution of 2 Mpix.

From this location, the footage from the medium-range stationary system will be monitored in RBPC in Vršac, BPS (border police station) in Veliko Gradište and the head office of the MoI, so the supplier will be obliged to install one side of the 100 Mbit/s radio relay link at this location, which will connect the location of "Kusić" with the location of "Bela Crkva".

Kusić - Bela Crkva radio relay link

Video streams from this location would be recorded in the best quality at the central location of the Ministry of Interior of the Republic of Serbia in Belgrade on the central server for video surveillance, and streams of lower quality (minimum 720p) would be transmitted in real time from the central video server, through the telecommunications system of the Ministry of Interior, to the RBPC in Vršac and BPS in Velko Gradište.

For the purpose of calculating the capacity of the IT network, in order to transmit the video signal of cameras in real time at a minimum of 720p, a maximum of 3 Mb/s transmission path per video channel shall be available. A stationary system that needs more than 3 Mb/s transmission path, for the transmission of a video signal of 720p quality in real time, shall not be acceptable to the ordering party.

Conclusion:

At this location of "Kusić", it is necessary to deliver and install the following items:

1.	One medium-range stationary system (thermal imaging camera + day/night camera)

2. four WDR Bullet IP cameras

3. one switch

4. one WEB relay

5.	One UPS 19" rack

6.	One side of the radio relay link with a capacity of 100 Mbit/s to connect this location with the "Bela Crkva" location

7.	One 15U communication cabinet for external mounting with air conditioning

8.	One steel telecommunications pole of 24m with foundations (lattice with platform)

9.	Wire panel fence with gate and backfilling of the fenced area

## “BPS in Veliko Gradište“ LOCATION

The location of the "BPS in Veliko Gradište" is located in the territory of the Municipality of Veliko Gradište. The local coordination centre (LCC) for the protection of the state border with the Republic of Romania is planned to be built at that location. For this purpose, it is necessary to provide one set for monitoring the operation of stationary systems for state border surveillance.

Furthermore, it is necessary to provide a UPS device for uninterrupted power supply in order for the Centre to be functional even in the event of a power outage. In the area (LCC) where the workstation and LCD TV are being installed, it is necessary to perform the installation of high and low current.

The installation of low current should be carried out in such a manner as to provide six RJ45 connectors. The connectors are installed in such a manner that the UTP cable Cat. 6 runs from the room of the RCC to the communication cabinet in the border police facility. UTP cables are laid in wall ducts and end on one side at wall sockets, and on the other at the patch panel with the corresponding number of ports in the communication cabinet. The installed connectors must be marked and the installation must be measured. The average distance between the LCC room and the communication cabinet is 60 meters.

The installation of high current should be carried out in such a manner to provide four 230V connectors. The connectors are installed so that the power cables are run through from the RCC room to the nearest power distribution cabinet in the regional centre building. Power cables are run through the wall ducts and end in wall sockets on one side, and on a separate fuse in the distribution cabinet. The connector in the distribution cabinet is installed from the field

for aggregate power supply (if there is one). The power of installed connectors must be sufficient to power a UPS device of at least 4.5 kW. Installed connectors must be marked. The average distance between the LCC room and the current distribution cabinet is 50 meters.

The location is connected to the MoI telecommunications network.

At the location (LCC) of the border police centres in the border police station in Veliki Gradište, the following items must be delivered and installed:

1. One workstation with accompanying surveillance software

2. Three monitors of minimum 23.5"

3. One LCD screen on the wall, of minimum 65"

4. One UPS

5. One desk

6. Two chairs

7. High and low current installation

8. One cabinet

# COMPREHENSIVE LIST OF REQUIRED EQUIPMENT

The table shows a recapitulation of the equipment for the implementation of this Project within the scope of ​​competence of the Regional Border Police Centre towards the Republic of Romania.

|  | Item / Location of installation | Location "Vrbica" | Location "Srpska Crnja" | Location "Jaša Tomić" | Location "Veliki Gaj" | Location "Kusić" | Location Bela Crkva | Location Vršački Breg | Location Krajišnik | Location Kikinda 2 | PU Kikinda | RCGP Vršac (RKC) | SGP Veliko Gradište | MUP, Kneza Miloša 101, Belgrade | In total |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1. | Medium-range stationary system (thermal imaging camera - day/night camera) | 1 | 1 | 1 | 1 | 1 |  |  |  |  |  |  |  |  | 5 |
| 2. | Telecommunication pole 24 m | 1 | 1 | 1 | 1 | 1 |  |  |  |  |  |  |  |  | 5 |
| 3. | WDR Bullet IP camera | 4 | 4 | 4 | 4 | 4 |  |  |  |  |  |  |  |  | 20 |
| 4. | Central video server and video management software (VMS) |  |  |  |  |  |  |  |  |  |  |  |  | 1 | 1 |
| 5. | Camera monitoring workstation for monitoring and managing cameras with support for simultaneous operation |  |  |  |  |  |  |  |  |  |  | 1 | 1 |  | 2 |
| 6. | Monitor minimum 23.5" LCD LED |  |  |  |  |  |  |  |  |  |  | 3 | 3 |  | 6 |
| 7. | LCD screen minimum 65" |  |  |  |  |  |  |  |  |  |  | 1 | 1 |  | 2 |
| 8. | Work table for LCC and RCC |  |  |  |  |  |  |  |  |  |  | 1 | 1 |  | 2 |
| 9. | Work chairs for LCC and RCC |  |  |  |  |  |  |  |  |  |  | 2 | 2 |  | 4 |
| 10. | Microwave radio equipment - Split-mount edge node - indoor unit | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 1 | 2 | 1 | 1 |  | 2 | 13+2 |
| 11a. | Microwave radio equipment - Split-mount outdoor unit (14641-14725 MHz) – TX Low | 1 | 1 |  | 2 |  | 2 |  | 1 |  | 1 | 1 |  | 2 | 9+2 |
| 11b | Microwave radio equipment - Split-mount outdoor unit (15061-15145 MHz) – TX High |  |  | 2 |  | 1 |  | 3 |  | 3 |  |  |  | 2 | 9+2 |
| 12. | Microwave antenna 0.3m (14620-15230 MHz) |  |  |  |  |  | 1 | 1 |  | 1 | 1 | 1 |  | 1 | 5+1 |
| 13. | Microwave antenna 0.6m (14620-15230 MHz) | 1 | 1 | 2 | 2 | 1 | 1 | 2 | 1 | 2 |  |  |  | 1 | 13+1 |
| 14. | Capacity License 100Mbps for Microwave radio equipment | 2 | 2 | 2 | 2 | 2 | 2 | 4 | 2 | 4 | 2 | 2 |  | 2 | 26+2 |
| 15. | 2nd Modem Activation (license) for Microwave radio equipment | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 1 | 2 | 1 | 1 |  | 2 | 13+2 |
| 16. | Switching Activation (license) for Microwave radio equipment | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 1 | 2 | 1 | 1 |  | 2 | 13+2 |
| 17. | Network switch | 1 | 1 | 1 | 1 | 1 |  |  |  |  |  |  |  |  | 5 |
| 18. | UPS - Uninterruptible power supply device - 19" rack variant | 1 | 1 | 1 | 1 | 1 |  |  |  |  |  |  |  |  | 5 |
| 19. | UPS - Uninterruptible power supply device – free-standing |  |  |  |  |  |  |  |  |  |  | 1 | 1 |  | 2 |
| 20. | WEB relay | 1 | 1 | 1 | 1 | 1 |  |  |  |  |  |  |  |  | 5 |
| 21. | Communication cabinet 15U external | 1 | 1 | 1 | 1 | 1 |  |  |  |  |  |  |  |  | 5 |
| 22. | Column height of 5m |  |  |  |  |  | 1 |  | 1 | 1 | 1 | 1 |  |  | 5 |
| 23. | Wire panel fence | 1 | 1 | 1 | 1 | 1 |  |  |  |  |  |  |  |  | 5 |